|  |  | Report according to EN 50160 2011 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Customer |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Auditor |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Name: |  |  |  |  |  |  |  |  |  |  | St.110/20kV Gai |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Name: |  |  |  |  |  |  |  |  | PC |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Company: |  |  |  |  |  |  |  |  |  |  | SC Enel Distributie Banat SA |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Company: |  |  |  |  |  |  |  |  | SC Enel Distributie Banat SA |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Location: |  |  |  |  |  |  |  |  |  |  | Arad jud.Arad |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | Start date: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 9/1/14 12:00 AM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | End date: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 3/1/15 11:59 PM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | Date: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 3/30/15 12:00 PM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | Software: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Janitza-GridVis 4.0.2(2013-05-28_14-34-52) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | UMG511 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | Device type: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | UMG511 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | EN 61000-4-7 Class: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Class 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | EN 61000-4-30 Class: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Class A |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | Flicker: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Supported |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | Events: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Supported |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | Transients: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Supported |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | Input Voltage (MediumVoltage): |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 20000.0V |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | Frequency: |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 50.0Hz |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | Relevant Voltages: |  |  |  |  |  |  |  |  |  |  |  |  |  |  | LL |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | Line selection: |  |  |  |  |  |  |  |  |  |  |  |  |  |  | L1 L2 L3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Report according to EN 50160 2011 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Timeframe:9/1/14 12:00 AM - 3/1/15 11:59 PM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1 / |  |  | 31 |  |  |  |  |  |  |
|  |  | Summary |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | Frequency +-1% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | Frequency -6%/+4% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | Voltage effective L2-L1 - 1st Test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | Voltage effective L2-L1 - 2nd Test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | Voltage effective L3-L2 - 1st Test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | Voltage effective L3-L2 - 2nd Test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | Voltage effective L1-L3 - 1st Test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | Voltage effective L1-L3 - 2nd Test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | THD U L2-L1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | THD U L3-L2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | THD U L1-L3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | Unbalance Voltage |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | Long term flicker L2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | Long term flicker L3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Failed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | Long term flicker L1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Failed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | Harmonics voltage (rel.) L2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | Harmonics voltage (rel.) L3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | Harmonics voltage (rel.) L1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | Undervoltage |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | Overvoltage |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Report according to EN 50160 2011 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Timeframe:9/1/14 12:00 AM - 3/1/15 11:59 PM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 2 / |  |  | 31 |  |  |  |  |  |  |
|  |  | Frequency +-1% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Limits |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Lower limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 49.50Hz |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Higher limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 50.50Hz |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Percentage |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 99.50% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Results |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Min value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 48.42Hz |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Average value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 50.00Hz |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Max value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 51.23Hz |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Undercut |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.10% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Overcut |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Total out |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.11% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Result |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Recording vacancy |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 32.97% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Norm Frequency (10s) [UMG511] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Marker Lower limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Marker Higher limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Report according to EN 50160 2011 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Timeframe:9/1/14 12:00 AM - 3/1/15 11:59 PM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 3 / |  |  | 31 |  |  |  |  |  |  |  |
|  |  | Frequency -6%/+4% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Limits |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Lower limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 47.00Hz |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Higher limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 52.00Hz |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Percentage |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 100.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Results |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Min value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 48.42Hz |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Average value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 50.00Hz |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Max value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 51.23Hz |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Undercut |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Overcut |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Total out |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Result |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Recording vacancy |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 32.97% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Norm Frequency (10s) [UMG511] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Marker Lower limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Marker Higher limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Report according to EN 50160 2011 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Timeframe:9/1/14 12:00 AM - 3/1/15 11:59 PM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 4 / |  |  | 31 |  |  |  |  |  |  |  |
|  |  | Voltage effective L2-L1 - 1st Test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Limits |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Lower limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 18000.00V |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Higher limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 22000.00V |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Percentage |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 99.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Results |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Min value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1.84V |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Average value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 20930.72V |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Max value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 21767.26V |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Undercut |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.26% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Overcut |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Total out |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.26% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Result |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Recording vacancy |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Voltage effective L2-L1 (10m) [UMG511] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Marker Lower limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Marker Higher limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Report according to EN 50160 2011 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Timeframe:9/1/14 12:00 AM - 3/1/15 11:59 PM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 5 / |  |  | 31 |  |  |  |  |  |  |  |
|  |  | Voltage effective L2-L1 - 2nd Test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Limits |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Lower limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 17000.00V |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Higher limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 23000.00V |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Percentage |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 100.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Results |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Min value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1.84V |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Average value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 20930.72V |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Max value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 21767.26V |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Undercut |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Overcut |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Total out |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Result |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Recording vacancy |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Voltage effective L2-L1 (10m) [UMG511] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Marker Lower limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Marker Higher limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Report according to EN 50160 2011 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Timeframe:9/1/14 12:00 AM - 3/1/15 11:59 PM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 6 / |  |  | 31 |  |  |  |  |  |  |  |
|  |  | Voltage effective L3-L2 - 1st Test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Limits |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Lower limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 18000.00V |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Higher limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 22000.00V |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Percentage |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 99.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Results |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Min value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1.95V |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Average value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 21050.77V |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Max value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 21906.20V |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Undercut |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.26% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Overcut |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Total out |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.26% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Result |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Recording vacancy |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Voltage effective L3-L2 (10m) [UMG511] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Marker Lower limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Marker Higher limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Report according to EN 50160 2011 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Timeframe:9/1/14 12:00 AM - 3/1/15 11:59 PM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 7 / |  |  | 31 |  |  |  |  |  |  |  |
|  |  | Voltage effective L3-L2 - 2nd Test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Limits |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Lower limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 17000.00V |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Higher limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 23000.00V |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Percentage |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 100.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Results |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Min value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1.95V |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Average value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 21050.77V |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Max value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 21906.20V |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Undercut |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Overcut |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Total out |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Result |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Recording vacancy |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Voltage effective L3-L2 (10m) [UMG511] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Marker Lower limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Marker Higher limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Report according to EN 50160 2011 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Timeframe:9/1/14 12:00 AM - 3/1/15 11:59 PM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 8 / |  |  | 31 |  |  |  |  |  |  |  |
|  |  | Voltage effective L1-L3 - 1st Test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Limits |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Lower limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 18000.00V |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Higher limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 22000.00V |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Percentage |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 99.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Results |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Min value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1.89V |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Average value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 21052.35V |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Max value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 21893.76V |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Undercut |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.26% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Overcut |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Total out |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.26% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Result |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Recording vacancy |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Voltage effective L1-L3 (10m) [UMG511] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Marker Lower limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Marker Higher limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Report according to EN 50160 2011 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Timeframe:9/1/14 12:00 AM - 3/1/15 11:59 PM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 9 / |  |  | 31 |  |  |  |  |  |  |  |
|  |  | Voltage effective L1-L3 - 2nd Test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Limits |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Lower limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 17000.00V |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Higher limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 23000.00V |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Percentage |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 100.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Results |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Min value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1.89V |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Average value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 21052.35V |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Max value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 21893.76V |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Undercut |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Overcut |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Total out |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Result |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Recording vacancy |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Voltage effective L1-L3 (10m) [UMG511] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Marker Lower limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Marker Higher limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Report according to EN 50160 2011 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Timeframe:9/1/14 12:00 AM - 3/1/15 11:59 PM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 10 / |  |  | 31 |  |  |  |  |  |  |  |
|  |  | THD U L2-L1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Limits |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Lower limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  | -- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Higher limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 8.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Percentage |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Results |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Min value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.39% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Average value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 2.11% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Max value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1028.80% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Undercut |  |  |  |  |  |  |  |  |  |  |  |  |  |  | -- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Overcut |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.29% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Total out |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.29% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Result |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Recording vacancy |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | THD U L2-L1 (10m) [UMG511] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Marker Higher limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Report according to EN 50160 2011 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Timeframe:9/1/14 12:00 AM - 3/1/15 11:59 PM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 11 / |  |  | 31 |  |  |  |  |  |  |  |
|  |  | THD U L3-L2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Limits |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Lower limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  | -- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Higher limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 8.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Percentage |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Results |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Min value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.31% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Average value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 2.53% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Max value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1080.05% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Undercut |  |  |  |  |  |  |  |  |  |  |  |  |  |  | -- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Overcut |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.29% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Total out |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.29% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Result |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Recording vacancy |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | THD U L3-L2 (10m) [UMG511] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Marker Higher limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Report according to EN 50160 2011 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Timeframe:9/1/14 12:00 AM - 3/1/15 11:59 PM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 12 / |  |  | 31 |  |  |  |  |  |  |  |
|  |  | THD U L1-L3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Limits |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Lower limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  | -- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Higher limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 8.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Percentage |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Results |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Min value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.39% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Average value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 2.15% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Max value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1067.60% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Undercut |  |  |  |  |  |  |  |  |  |  |  |  |  |  | -- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Overcut |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.29% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Total out |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.29% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Result |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Recording vacancy |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | THD U L1-L3 (10m) [UMG511] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Marker Higher limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Report according to EN 50160 2011 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Timeframe:9/1/14 12:00 AM - 3/1/15 11:59 PM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 13 / |  |  | 31 |  |  |  |  |  |  |  |
|  |  | Unbalance Voltage |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Limits |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Lower limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  | -- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Higher limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 2.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Percentage |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Results |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Min value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Average value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.42% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Max value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 43.08% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Undercut |  |  |  |  |  |  |  |  |  |  |  |  |  |  | -- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Overcut |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.07% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Total out |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.07% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Result |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Recording vacancy |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Unbalance Voltage (10m) [UMG511] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Marker Higher limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Report according to EN 50160 2011 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Timeframe:9/1/14 12:00 AM - 3/1/15 11:59 PM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 14 / |  |  | 31 |  |  |  |  |  |  |  |
|  |  | Long term flicker L2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Limits |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Lower limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  | -- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Higher limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Percentage |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Results |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Min value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.08 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Average value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.42 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Max value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 4.93 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Undercut |  |  |  |  |  |  |  |  |  |  |  |  |  |  | -- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Overcut |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 4.84% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Total out |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 4.84% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Result |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Recording vacancy |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1.63% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Long term flicker L2 (2h) [UMG511] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Marker Higher limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Report according to EN 50160 2011 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Timeframe:9/1/14 12:00 AM - 3/1/15 11:59 PM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 15 / |  |  | 31 |  |  |  |  |  |  |  |
|  |  | Long term flicker L3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Limits |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Lower limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  | -- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Higher limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Percentage |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Results |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Min value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.08 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Average value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.42 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Max value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 5.95 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Undercut |  |  |  |  |  |  |  |  |  |  |  |  |  |  | -- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Overcut |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 5.49% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Total out |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 5.49% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Result |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Failed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Recording vacancy |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1.63% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Long term flicker L3 (2h) [UMG511] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Marker Higher limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Report according to EN 50160 2011 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Timeframe:9/1/14 12:00 AM - 3/1/15 11:59 PM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 16 / |  |  | 31 |  |  |  |  |  |  |  |
|  |  | Long term flicker L1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Limits |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Lower limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  | -- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Higher limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Percentage |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Results |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Min value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.08 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Average value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.43 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Max value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 6.14 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Undercut |  |  |  |  |  |  |  |  |  |  |  |  |  |  | -- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Overcut |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 5.67% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Total out |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 5.67% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Result |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Failed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Recording vacancy |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1.63% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Long term flicker L1 (2h) [UMG511] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Marker Higher limit |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Report according to EN 50160 2011 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Timeframe:9/1/14 12:00 AM - 3/1/15 11:59 PM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 17 / |  |  | 31 |  |  |  |  |  |  |  |
|  |  | Harmonics voltage (rel.) L2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Value |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Higher limit |  |  |  |  |  |  |  |  | Min value |  |  |  |  |  |  |  |  | Overcut |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Average value |  |  |  |  |  |  |  |  | Recording vacancy |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Percentage |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Max value |  |  |  |  |  |  |  |  | Result |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 2.Harmonic Voltage L2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 2.00% |  |  |  |  |  |  |  |  | 0.02% |  |  |  |  |  |  |  |  | 0.21% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.10% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 87.19% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 3.Harmonic Voltage L2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 5.00% |  |  |  |  |  |  |  |  | 0.03% |  |  |  |  |  |  |  |  | 0.21% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.18% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 82.59% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 4.Harmonic Voltage L2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1.00% |  |  |  |  |  |  |  |  | 0.02% |  |  |  |  |  |  |  |  | 0.21% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.09% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 96.98% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 5.Harmonic Voltage L2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 6.00% |  |  |  |  |  |  |  |  | 0.07% |  |  |  |  |  |  |  |  | 0.12% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1.06% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 78.56% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 6.Harmonic Voltage L2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.50% |  |  |  |  |  |  |  |  | 0.02% |  |  |  |  |  |  |  |  | 0.21% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.08% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 77.88% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 7.Harmonic Voltage L2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 5.00% |  |  |  |  |  |  |  |  | 0.05% |  |  |  |  |  |  |  |  | 0.11% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.41% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 76.18% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 8.Harmonic Voltage L2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.50% |  |  |  |  |  |  |  |  | 0.02% |  |  |  |  |  |  |  |  | 0.21% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.07% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 77.18% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 9.Harmonic Voltage L2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1.50% |  |  |  |  |  |  |  |  | 0.02% |  |  |  |  |  |  |  |  | 0.21% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.13% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 75.30% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 10.Harmonic Voltage L2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.50% |  |  |  |  |  |  |  |  | 0.01% |  |  |  |  |  |  |  |  | 0.21% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.07% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 75.32% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 11.Harmonic Voltage L2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 3.50% |  |  |  |  |  |  |  |  | 0.05% |  |  |  |  |  |  |  |  | 0.10% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.28% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 75.53% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 12.Harmonic Voltage L2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.50% |  |  |  |  |  |  |  |  | 0.01% |  |  |  |  |  |  |  |  | 0.21% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.07% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 74.26% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 13.Harmonic Voltage L2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 3.00% |  |  |  |  |  |  |  |  | 0.04% |  |  |  |  |  |  |  |  | 0.10% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.22% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 74.36% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 14.Harmonic Voltage L2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.50% |  |  |  |  |  |  |  |  | 0.01% |  |  |  |  |  |  |  |  | 0.21% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.07% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 73.40% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 15.Harmonic Voltage L2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.50% |  |  |  |  |  |  |  |  | 0.02% |  |  |  |  |  |  |  |  | 0.21% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.11% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 73.74% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 16.Harmonic Voltage L2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.50% |  |  |  |  |  |  |  |  | 0.01% |  |  |  |  |  |  |  |  | 0.21% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.07% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 74.45% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 17.Harmonic Voltage L2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 2.00% |  |  |  |  |  |  |  |  | 0.02% |  |  |  |  |  |  |  |  | 0.15% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.13% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 73.94% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 18.Harmonic Voltage L2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.50% |  |  |  |  |  |  |  |  | 0.01% |  |  |  |  |  |  |  |  | 0.21% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.06% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 74.29% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Report according to EN 50160 2011 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Timeframe:9/1/14 12:00 AM - 3/1/15 11:59 PM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 18 / |  |  | 31 |  |  |  |  |  |  |
|  |  |  |  |  | Value |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Higher limit |  |  |  |  |  |  |  |  | Min value |  |  |  |  |  |  |  |  | Overcut |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Average value |  |  |  |  |  |  |  |  | Recording vacancy |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Percentage |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Max value |  |  |  |  |  |  |  |  | Result |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 19.Harmonic Voltage L2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1.50% |  |  |  |  |  |  |  |  | 0.02% |  |  |  |  |  |  |  |  | 0.18% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.11% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 74.69% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 20.Harmonic Voltage L2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.50% |  |  |  |  |  |  |  |  | 0.01% |  |  |  |  |  |  |  |  | 0.21% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.06% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 74.62% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 21.Harmonic Voltage L2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.50% |  |  |  |  |  |  |  |  | 0.01% |  |  |  |  |  |  |  |  | 0.21% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.08% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 75.22% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 22.Harmonic Voltage L2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.50% |  |  |  |  |  |  |  |  | 0.01% |  |  |  |  |  |  |  |  | 0.21% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.06% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 75.69% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 23.Harmonic Voltage L2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1.50% |  |  |  |  |  |  |  |  | 0.01% |  |  |  |  |  |  |  |  | 0.17% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.09% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 75.59% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 24.Harmonic Voltage L2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.50% |  |  |  |  |  |  |  |  | 0.01% |  |  |  |  |  |  |  |  | 0.21% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.06% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 76.52% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 25.Harmonic Voltage L2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1.50% |  |  |  |  |  |  |  |  | 0.01% |  |  |  |  |  |  |  |  | 0.18% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.09% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 76.38% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Harmonics voltage L2 [UMG511] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Report according to EN 50160 2011 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Timeframe:9/1/14 12:00 AM - 3/1/15 11:59 PM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 19 / |  |  | 31 |  |  |  |  |  |  |  |  |
|  |  | Harmonics voltage (rel.) L3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Value |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Higher limit |  |  |  |  |  |  |  |  | Min value |  |  |  |  |  |  |  |  | Overcut |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Average value |  |  |  |  |  |  |  |  | Recording vacancy |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Percentage |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Max value |  |  |  |  |  |  |  |  | Result |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 2.Harmonic Voltage L3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 2.00% |  |  |  |  |  |  |  |  | 0.02% |  |  |  |  |  |  |  |  | 0.21% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.11% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 94.70% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 3.Harmonic Voltage L3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 5.00% |  |  |  |  |  |  |  |  | 0.06% |  |  |  |  |  |  |  |  | 0.17% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.26% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 79.74% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 4.Harmonic Voltage L3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1.00% |  |  |  |  |  |  |  |  | 0.02% |  |  |  |  |  |  |  |  | 0.20% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.09% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 84.16% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 5.Harmonic Voltage L3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 6.00% |  |  |  |  |  |  |  |  | 0.06% |  |  |  |  |  |  |  |  | 0.15% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1.02% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 77.14% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 6.Harmonic Voltage L3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.50% |  |  |  |  |  |  |  |  | 0.02% |  |  |  |  |  |  |  |  | 0.21% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.08% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 75.93% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 7.Harmonic Voltage L3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 5.00% |  |  |  |  |  |  |  |  | 0.04% |  |  |  |  |  |  |  |  | 0.15% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.41% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 74.91% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 8.Harmonic Voltage L3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.50% |  |  |  |  |  |  |  |  | 0.01% |  |  |  |  |  |  |  |  | 0.19% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.07% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 75.92% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 9.Harmonic Voltage L3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1.50% |  |  |  |  |  |  |  |  | 0.02% |  |  |  |  |  |  |  |  | 0.17% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.12% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 74.63% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 10.Harmonic Voltage L3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.50% |  |  |  |  |  |  |  |  | 0.01% |  |  |  |  |  |  |  |  | 0.18% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.07% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 73.12% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 11.Harmonic Voltage L3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 3.50% |  |  |  |  |  |  |  |  | 0.05% |  |  |  |  |  |  |  |  | 0.17% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.32% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 88.46% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 12.Harmonic Voltage L3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.50% |  |  |  |  |  |  |  |  | 0.01% |  |  |  |  |  |  |  |  | 0.18% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.07% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 98.50% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 13.Harmonic Voltage L3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 3.00% |  |  |  |  |  |  |  |  | 0.04% |  |  |  |  |  |  |  |  | 0.17% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.23% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 99.07% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 14.Harmonic Voltage L3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.50% |  |  |  |  |  |  |  |  | 0.01% |  |  |  |  |  |  |  |  | 0.17% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.07% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 94.20% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 15.Harmonic Voltage L3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.50% |  |  |  |  |  |  |  |  | 0.02% |  |  |  |  |  |  |  |  | 0.17% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.11% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 100.97% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 16.Harmonic Voltage L3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.50% |  |  |  |  |  |  |  |  | 0.01% |  |  |  |  |  |  |  |  | 0.17% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.07% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 93.21% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 17.Harmonic Voltage L3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 2.00% |  |  |  |  |  |  |  |  | 0.02% |  |  |  |  |  |  |  |  | 0.17% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.12% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 86.12% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 18.Harmonic Voltage L3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.50% |  |  |  |  |  |  |  |  | 0.01% |  |  |  |  |  |  |  |  | 0.17% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.07% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 101.51% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Report according to EN 50160 2011 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Timeframe:9/1/14 12:00 AM - 3/1/15 11:59 PM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 20 / |  |  | 31 |  |  |  |  |  |  |
|  |  |  |  |  | Value |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Higher limit |  |  |  |  |  |  |  |  | Min value |  |  |  |  |  |  |  |  | Overcut |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Average value |  |  |  |  |  |  |  |  | Recording vacancy |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Percentage |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Max value |  |  |  |  |  |  |  |  | Result |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 19.Harmonic Voltage L3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1.50% |  |  |  |  |  |  |  |  | 0.01% |  |  |  |  |  |  |  |  | 0.17% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.12% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 108.26% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 20.Harmonic Voltage L3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.50% |  |  |  |  |  |  |  |  | 0.01% |  |  |  |  |  |  |  |  | 0.17% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.07% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 110.17% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 21.Harmonic Voltage L3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.50% |  |  |  |  |  |  |  |  | 0.01% |  |  |  |  |  |  |  |  | 0.17% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.09% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 120.16% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 22.Harmonic Voltage L3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.50% |  |  |  |  |  |  |  |  | 0.01% |  |  |  |  |  |  |  |  | 0.17% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.07% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 115.42% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 23.Harmonic Voltage L3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1.50% |  |  |  |  |  |  |  |  | 0.01% |  |  |  |  |  |  |  |  | 0.17% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.10% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 108.82% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 24.Harmonic Voltage L3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.50% |  |  |  |  |  |  |  |  | 0.01% |  |  |  |  |  |  |  |  | 0.17% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.07% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 101.97% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 25.Harmonic Voltage L3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1.50% |  |  |  |  |  |  |  |  | 0.01% |  |  |  |  |  |  |  |  | 0.17% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.10% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 105.62% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Harmonics voltage L3 [UMG511] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Report according to EN 50160 2011 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Timeframe:9/1/14 12:00 AM - 3/1/15 11:59 PM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 21 / |  |  | 31 |  |  |  |  |  |  |  |  |
|  |  | Harmonics voltage (rel.) L1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Value |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Higher limit |  |  |  |  |  |  |  |  | Min value |  |  |  |  |  |  |  |  | Overcut |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Average value |  |  |  |  |  |  |  |  | Recording vacancy |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Percentage |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Max value |  |  |  |  |  |  |  |  | Result |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 2.Harmonic Voltage L1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 2.00% |  |  |  |  |  |  |  |  | 0.02% |  |  |  |  |  |  |  |  | 0.21% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.10% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 89.77% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 3.Harmonic Voltage L1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 5.00% |  |  |  |  |  |  |  |  | 0.07% |  |  |  |  |  |  |  |  | 0.17% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.31% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 78.13% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 4.Harmonic Voltage L1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1.00% |  |  |  |  |  |  |  |  | 0.02% |  |  |  |  |  |  |  |  | 0.19% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.08% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 79.97% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 5.Harmonic Voltage L1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 6.00% |  |  |  |  |  |  |  |  | 0.06% |  |  |  |  |  |  |  |  | 0.16% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.98% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 73.93% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 6.Harmonic Voltage L1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.50% |  |  |  |  |  |  |  |  | 0.02% |  |  |  |  |  |  |  |  | 0.21% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.07% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 73.65% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 7.Harmonic Voltage L1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 5.00% |  |  |  |  |  |  |  |  | 0.05% |  |  |  |  |  |  |  |  | 0.15% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.44% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 71.83% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 8.Harmonic Voltage L1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.50% |  |  |  |  |  |  |  |  | 0.02% |  |  |  |  |  |  |  |  | 0.18% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.07% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 71.61% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 9.Harmonic Voltage L1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1.50% |  |  |  |  |  |  |  |  | 0.02% |  |  |  |  |  |  |  |  | 0.17% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.15% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 70.75% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 10.Harmonic Voltage L1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.50% |  |  |  |  |  |  |  |  | 0.01% |  |  |  |  |  |  |  |  | 0.18% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.06% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 69.80% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 11.Harmonic Voltage L1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 3.50% |  |  |  |  |  |  |  |  | 0.07% |  |  |  |  |  |  |  |  | 0.17% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.33% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 69.74% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 12.Harmonic Voltage L1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.50% |  |  |  |  |  |  |  |  | 0.01% |  |  |  |  |  |  |  |  | 0.17% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.06% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 69.34% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 13.Harmonic Voltage L1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 3.00% |  |  |  |  |  |  |  |  | 0.04% |  |  |  |  |  |  |  |  | 0.17% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.23% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 68.55% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 14.Harmonic Voltage L1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.50% |  |  |  |  |  |  |  |  | 0.01% |  |  |  |  |  |  |  |  | 0.17% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.07% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 68.24% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 15.Harmonic Voltage L1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.50% |  |  |  |  |  |  |  |  | 0.02% |  |  |  |  |  |  |  |  | 0.17% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.13% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 68.14% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 16.Harmonic Voltage L1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.50% |  |  |  |  |  |  |  |  | 0.01% |  |  |  |  |  |  |  |  | 0.17% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.06% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 67.76% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 17.Harmonic Voltage L1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 2.00% |  |  |  |  |  |  |  |  | 0.02% |  |  |  |  |  |  |  |  | 0.17% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.14% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 67.89% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 18.Harmonic Voltage L1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.50% |  |  |  |  |  |  |  |  | 0.01% |  |  |  |  |  |  |  |  | 0.17% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.06% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 68.33% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Report according to EN 50160 2011 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Timeframe:9/1/14 12:00 AM - 3/1/15 11:59 PM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 22 / |  |  | 31 |  |  |  |  |  |  |
|  |  |  |  |  | Value |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Higher limit |  |  |  |  |  |  |  |  | Min value |  |  |  |  |  |  |  |  | Overcut |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Average value |  |  |  |  |  |  |  |  | Recording vacancy |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Percentage |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Max value |  |  |  |  |  |  |  |  | Result |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 19.Harmonic Voltage L1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1.50% |  |  |  |  |  |  |  |  | 0.02% |  |  |  |  |  |  |  |  | 0.17% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.11% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 69.02% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 20.Harmonic Voltage L1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.50% |  |  |  |  |  |  |  |  | 0.01% |  |  |  |  |  |  |  |  | 0.17% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.06% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 68.20% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 21.Harmonic Voltage L1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.50% |  |  |  |  |  |  |  |  | 0.01% |  |  |  |  |  |  |  |  | 0.17% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.08% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 68.90% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 22.Harmonic Voltage L1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.50% |  |  |  |  |  |  |  |  | 0.01% |  |  |  |  |  |  |  |  | 0.17% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.06% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 69.78% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 23.Harmonic Voltage L1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1.50% |  |  |  |  |  |  |  |  | 0.02% |  |  |  |  |  |  |  |  | 0.17% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.10% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 69.49% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 24.Harmonic Voltage L1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.50% |  |  |  |  |  |  |  |  | 0.01% |  |  |  |  |  |  |  |  | 0.17% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.06% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 69.02% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 25.Harmonic Voltage L1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1.50% |  |  |  |  |  |  |  |  | 0.02% |  |  |  |  |  |  |  |  | 0.17% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.09% |  |  |  |  |  |  |  |  | 33.25% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 95.00% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 69.12% |  |  |  |  |  |  |  |  | Passed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Harmonics voltage L1 [UMG511] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Report according to EN 50160 2011 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Timeframe:9/1/14 12:00 AM - 3/1/15 11:59 PM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 23 / |  |  | 31 |  |  |  |  |  |  |  |  |
|  |  | Undervoltage |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | 475 Events have been found. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | Residual voltage u % |  |  |  |  |  |  | Duration t |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 10 - 200ms |  |  |  |  |  |  | > 200ms |  |  |  | > 500ms |  |  |  |  |  | > 1s |  |  |  |  |  | > 5s - 60s |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | < 90 - 80 % |  |  |  |  |  |  | 0 |  |  |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  |  | 0 |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | < 80 - 70 % |  |  |  |  |  |  | 0 |  |  |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  |  | 0 |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | < 70 - 40 % |  |  |  |  |  |  | 0 |  |  |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  |  | 0 |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | < 40 - 5 % |  |  |  |  |  |  | 0 |  |  |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  |  | 0 |  |  |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | < 5 % |  |  |  |  |  |  | 220 |  |  |  |  |  |  | 44 |  |  |  | 13 |  |  |  |  |  | 14 |  |  |  |  |  | 33 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 151 out of ranges! |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Starttime |  |  |  |  |  |  |  |  |  |  |  | Length |  |  |  |  |  |  |  |  | Input |  |  | Eventtype |  |  |  |  |  | Limit |  |  |  |  | Min |  |  |  |  |  | Avg |  | Max |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Endtime |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/3/14 3:30:58 PM'898 |  |  |  |  |  |  |  |  |  |  |  | 1m 0s |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 8.41 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/3/14 3:31:59 PM'212 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/3/14 3:35:28 PM'360 |  |  |  |  |  |  |  |  |  |  |  | 38.657s |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 8.41 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/3/14 3:36:07 PM'017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/18/14 12:35:59 PM'649 |  |  |  |  |  |  |  |  |  |  |  | 31.901ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/18/14 12:35:59 PM'681 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/18/14 12:36:00 PM'335 |  |  |  |  |  |  |  |  |  |  |  | 96.505ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/18/14 12:36:00 PM'432 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/18/14 12:36:00 PM'977 |  |  |  |  |  |  |  |  |  |  |  | 274.912ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 8.41 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/18/14 12:36:01 PM'252 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/18/14 12:36:01 PM'465 |  |  |  |  |  |  |  |  |  |  |  | 1m 57s |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/18/14 12:37:58 PM'705 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/26/14 9:32:28 AM'498 |  |  |  |  |  |  |  |  |  |  |  | 82.604ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/26/14 9:32:28 AM'581 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/26/14 9:32:29 AM'115 |  |  |  |  |  |  |  |  |  |  |  | 14.133s |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/26/14 9:32:43 AM'249 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/26/14 6:37:27 PM'857 |  |  |  |  |  |  |  |  |  |  |  | 30.151ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/26/14 6:37:27 PM'887 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/26/14 6:37:28 PM'555 |  |  |  |  |  |  |  |  |  |  |  | 79.103ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/26/14 6:37:28 PM'634 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/26/14 6:37:29 PM'203 |  |  |  |  |  |  |  |  |  |  |  | 189.308ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 8.41 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/26/14 6:37:29 PM'393 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/26/14 6:37:29 PM'790 |  |  |  |  |  |  |  |  |  |  |  | 1h 17m |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/26/14 7:54:49 PM'277 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/5/14 10:24:36 AM'478 |  |  |  |  |  |  |  |  |  |  |  | 49.603ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/5/14 10:24:36 AM'528 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/5/14 10:24:37 AM'144 |  |  |  |  |  |  |  |  |  |  |  | 170.806ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 8.41 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/5/14 10:24:37 AM'315 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/5/14 10:24:37 AM'656 |  |  |  |  |  |  |  |  |  |  |  | 3m 45s |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/5/14 10:28:23 AM'472 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/16/14 3:15:47 PM'441 |  |  |  |  |  |  |  |  |  |  |  | 2m 12s |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/16/14 3:18:00 PM'267 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/26/14 1:30:35 PM'372 |  |  |  |  |  |  |  |  |  |  |  | 39.101ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/26/14 1:30:35 PM'411 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/26/14 1:30:36 PM'021 |  |  |  |  |  |  |  |  |  |  |  | 79.904ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/26/14 1:30:36 PM'101 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/26/14 1:30:36 PM'687 |  |  |  |  |  |  |  |  |  |  |  | 207.058ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/26/14 1:30:36 PM'894 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/26/14 1:30:37 PM'178 |  |  |  |  |  |  |  |  |  |  |  | 44m 37s |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/26/14 2:15:14 PM'344 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/27/14 12:14:02 PM'294 |  |  |  |  |  |  |  |  |  |  |  | 49.802ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/27/14 12:14:02 PM'344 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/27/14 12:14:03 PM'001 |  |  |  |  |  |  |  |  |  |  |  | 110.605ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/27/14 12:14:03 PM'112 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/27/14 12:14:03 PM'754 |  |  |  |  |  |  |  |  |  |  |  | 53.600s |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/27/14 12:14:57 PM'354 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/29/14 9:55:47 AM'430 |  |  |  |  |  |  |  |  |  |  |  | 40.603ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/29/14 9:55:47 AM'471 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Report according to EN 50160 2011 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Timeframe:9/1/14 12:00 AM - 3/1/15 11:59 PM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 24 / |  |  | 31 |  |  |  |  |  |  |
|  |  |  | Starttime |  |  |  |  |  |  |  |  |  |  |  | Length |  |  |  |  |  |  |  |  | Input |  |  | Eventtype |  |  |  |  |  | Limit |  |  |  |  | Min |  |  |  |  |  | Avg |  | Max |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Endtime |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/29/14 9:55:48 AM'121 |  |  |  |  |  |  |  |  |  |  |  | 102.354ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/29/14 9:55:48 AM'223 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/29/14 9:55:48 AM'665 |  |  |  |  |  |  |  |  |  |  |  | 244.660ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/29/14 9:55:48 AM'910 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/29/14 9:55:49 AM'214 |  |  |  |  |  |  |  |  |  |  |  | 53.261s |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/29/14 9:56:42 AM'475 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/1/14 2:09:48 PM'388 |  |  |  |  |  |  |  |  |  |  |  | 40.653ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/1/14 2:09:48 PM'429 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/1/14 2:09:49 PM'038 |  |  |  |  |  |  |  |  |  |  |  | 82.354ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/1/14 2:09:49 PM'120 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/1/14 2:09:49 PM'696 |  |  |  |  |  |  |  |  |  |  |  | 204.309ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 8.41 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/1/14 2:09:49 PM'901 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/1/14 2:09:50 PM'184 |  |  |  |  |  |  |  |  |  |  |  | 9m 39s |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 8.41 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/1/14 2:19:29 PM'224 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/2/14 11:08:36 AM'766 |  |  |  |  |  |  |  |  |  |  |  | 39.302ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/2/14 11:08:36 AM'806 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/2/14 11:08:37 AM'421 |  |  |  |  |  |  |  |  |  |  |  | 89.204ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 8.41 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/2/14 11:08:37 AM'510 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/3/14 12:27:13 PM'020 |  |  |  |  |  |  |  |  |  |  |  | 31.602ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/3/14 12:27:13 PM'052 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/3/14 12:27:13 PM'674 |  |  |  |  |  |  |  |  |  |  |  | 84.154ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 8.41 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/3/14 12:27:13 PM'758 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/18/14 9:35:09 PM'952 |  |  |  |  |  |  |  |  |  |  |  | 19.702ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/18/14 9:35:09 PM'972 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/18/14 9:35:10 PM'357 |  |  |  |  |  |  |  |  |  |  |  | 4.530s |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 5.95 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/18/14 9:35:14 PM'887 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/3/14 8:38:24 AM'020 |  |  |  |  |  |  |  |  |  |  |  | 61.101ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/3/14 8:38:24 AM'081 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/3/14 8:38:24 AM'634 |  |  |  |  |  |  |  |  |  |  |  | 6m 1s |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 8.41 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/3/14 8:44:26 AM'594 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/3/14 12:39:31 PM'230 |  |  |  |  |  |  |  |  |  |  |  | 59.351ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/3/14 12:39:31 PM'289 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/3/14 12:39:31 PM'939 |  |  |  |  |  |  |  |  |  |  |  | 179.001ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 8.41 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/3/14 12:39:32 PM'118 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/3/14 12:39:32 PM'475 |  |  |  |  |  |  |  |  |  |  |  | 3.021s |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 5.95 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/3/14 12:39:35 PM'497 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/3/14 2:51:08 PM'587 |  |  |  |  |  |  |  |  |  |  |  | 40.401ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/3/14 2:51:08 PM'627 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/3/14 2:51:09 PM'110 |  |  |  |  |  |  |  |  |  |  |  | 109.950ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/3/14 2:51:09 PM'220 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/3/14 2:51:09 PM'488 |  |  |  |  |  |  |  |  |  |  |  | 857.053ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/3/14 2:51:10 PM'345 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/10/14 10:04:28 AM'322 |  |  |  |  |  |  |  |  |  |  |  | 9.951ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/10/14 10:04:28 AM'332 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/10/14 10:04:28 AM'452 |  |  |  |  |  |  |  |  |  |  |  | 1h 13m |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/10/14 11:18:11 AM'029 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/11/14 9:44:07 AM'416 |  |  |  |  |  |  |  |  |  |  |  | 628.410ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 5.95 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/11/14 9:44:08 AM'044 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/11/14 9:44:08 AM'093 |  |  |  |  |  |  |  |  |  |  |  | 1h 51m |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/11/14 11:35:10 AM'010 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/10/15 12:55:38 PM'995 |  |  |  |  |  |  |  |  |  |  |  | 1m 28s |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/10/15 12:57:07 PM'916 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/10/15 12:58:41 PM'636 |  |  |  |  |  |  |  |  |  |  |  | 2m 5s |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 8.41 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/10/15 1:00:47 PM'559 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/10/15 1:02:29 PM'285 |  |  |  |  |  |  |  |  |  |  |  | 1m 8s |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 5.95 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/10/15 1:03:37 PM'937 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/10/15 1:03:57 PM'179 |  |  |  |  |  |  |  |  |  |  |  | 5m 51s |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/10/15 1:09:48 PM'187 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:02:39 AM'118 |  |  |  |  |  |  |  |  |  |  |  | 49.701ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:02:39 AM'168 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:02:39 AM'847 |  |  |  |  |  |  |  |  |  |  |  | 129.351ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:02:39 AM'976 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:02:40 AM'414 |  |  |  |  |  |  |  |  |  |  |  | 330.051ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 5.95 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:02:40 AM'744 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:02:40 AM'904 |  |  |  |  |  |  |  |  |  |  |  | 27.725s |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 5.95 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:03:08 AM'630 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:03:10 AM'056 |  |  |  |  |  |  |  |  |  |  |  | 40.001ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:03:10 AM'096 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:03:10 AM'728 |  |  |  |  |  |  |  |  |  |  |  | 89.350ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:03:10 AM'818 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Report according to EN 50160 2011 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Timeframe:9/1/14 12:00 AM - 3/1/15 11:59 PM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 25 / |  |  | 31 |  |  |  |  |  |  |
|  |  |  | Starttime |  |  |  |  |  |  |  |  |  |  |  | Length |  |  |  |  |  |  |  |  | Input |  |  | Eventtype |  |  |  |  |  | Limit |  |  |  |  | Min |  |  |  |  |  | Avg |  | Max |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Endtime |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:03:11 AM'452 |  |  |  |  |  |  |  |  |  |  |  | 307.750ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 8.41 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:03:11 AM'760 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:03:11 AM'840 |  |  |  |  |  |  |  |  |  |  |  | 1m 25s |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:04:37 AM'020 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:04:38 AM'969 |  |  |  |  |  |  |  |  |  |  |  | 51.500ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:04:39 AM'021 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:04:39 AM'654 |  |  |  |  |  |  |  |  |  |  |  | 121.300ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 5.95 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:04:39 AM'775 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:04:40 AM'302 |  |  |  |  |  |  |  |  |  |  |  | 6m 20s |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:11:00 AM'565 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:11:02 AM'485 |  |  |  |  |  |  |  |  |  |  |  | 40.750ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:11:02 AM'526 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:11:03 AM'195 |  |  |  |  |  |  |  |  |  |  |  | 110.751ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:11:03 AM'306 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:11:03 AM'807 |  |  |  |  |  |  |  |  |  |  |  | 4m 6s |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 8.41 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:15:10 AM'700 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:15:12 AM'614 |  |  |  |  |  |  |  |  |  |  |  | 40.351ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 8.41 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:15:12 AM'654 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:15:13 AM'283 |  |  |  |  |  |  |  |  |  |  |  | 102.301ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 5.95 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:15:13 AM'385 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:15:13 AM'894 |  |  |  |  |  |  |  |  |  |  |  | 244.850ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 8.41 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:15:14 AM'139 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:15:14 AM'384 |  |  |  |  |  |  |  |  |  |  |  | 5m 1s |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:20:15 AM'421 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:20:17 AM'742 |  |  |  |  |  |  |  |  |  |  |  | 10.051ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:20:17 AM'752 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:20:17 AM'943 |  |  |  |  |  |  |  |  |  |  |  | 60.351ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 8.41 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:20:18 AM'003 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:20:18 AM'074 |  |  |  |  |  |  |  |  |  |  |  | 19m 14s |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:39:32 AM'944 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:39:34 AM'289 |  |  |  |  |  |  |  |  |  |  |  | 1m 18s |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:40:52 AM'916 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:40:54 AM'154 |  |  |  |  |  |  |  |  |  |  |  | 1h 20m |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 3:01:40 AM'900 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 3:01:42 AM'205 |  |  |  |  |  |  |  |  |  |  |  | 19.901ms |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 3:01:42 AM'225 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 3:01:42 AM'255 |  |  |  |  |  |  |  |  |  |  |  | 3m 34s |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 8.41 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 3:05:16 AM'663 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 3:05:16 AM'693 |  |  |  |  |  |  |  |  |  |  |  | 47m 33s |  |  |  |  |  |  |  |  | L1 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 8.41 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 3:52:50 AM'026 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/3/14 3:30:59 PM'899 |  |  |  |  |  |  |  |  |  |  |  | 59.378s |  |  |  |  |  |  |  |  | L2 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 5.95 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/3/14 3:31:59 PM'277 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/3/14 3:35:27 PM'998 |  |  |  |  |  |  |  |  |  |  |  | 38.921s |  |  |  |  |  |  |  |  | L2 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 8.41 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/3/14 3:36:06 PM'919 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/18/14 12:35:59 PM'632 |  |  |  |  |  |  |  |  |  |  |  | 42.452ms |  |  |  |  |  |  |  |  | L2 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 8.41 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/18/14 12:35:59 PM'674 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/18/14 12:36:00 PM'350 |  |  |  |  |  |  |  |  |  |  |  | 96.403ms |  |  |  |  |  |  |  |  | L2 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 8.41 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/18/14 12:36:00 PM'446 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/18/14 12:36:00 PM'938 |  |  |  |  |  |  |  |  |  |  |  | 233.009ms |  |  |  |  |  |  |  |  | L2 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/18/14 12:36:01 PM'171 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/18/14 12:36:01 PM'544 |  |  |  |  |  |  |  |  |  |  |  | 1m 57s |  |  |  |  |  |  |  |  | L2 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 8.41 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/18/14 12:37:58 PM'712 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/26/14 9:32:28 AM'492 |  |  |  |  |  |  |  |  |  |  |  | 92.955ms |  |  |  |  |  |  |  |  | L2 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/26/14 9:32:28 AM'585 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/26/14 9:32:29 AM'088 |  |  |  |  |  |  |  |  |  |  |  | 14.154s |  |  |  |  |  |  |  |  | L2 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 8.41 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/26/14 9:32:43 AM'242 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/26/14 6:37:27 PM'850 |  |  |  |  |  |  |  |  |  |  |  | 40.252ms |  |  |  |  |  |  |  |  | L2 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/26/14 6:37:27 PM'890 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/26/14 6:37:28 PM'548 |  |  |  |  |  |  |  |  |  |  |  | 88.954ms |  |  |  |  |  |  |  |  | L2 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/26/14 6:37:28 PM'637 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/26/14 6:37:29 PM'187 |  |  |  |  |  |  |  |  |  |  |  | 179.408ms |  |  |  |  |  |  |  |  | L2 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/26/14 6:37:29 PM'366 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/26/14 6:37:29 PM'814 |  |  |  |  |  |  |  |  |  |  |  | 1h 17m |  |  |  |  |  |  |  |  | L2 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/26/14 7:54:49 PM'284 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/5/14 10:24:36 AM'462 |  |  |  |  |  |  |  |  |  |  |  | 59.452ms |  |  |  |  |  |  |  |  | L2 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/5/14 10:24:36 AM'521 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/5/14 10:24:37 AM'158 |  |  |  |  |  |  |  |  |  |  |  | 180.858ms |  |  |  |  |  |  |  |  | L2 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 5.95 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/5/14 10:24:37 AM'339 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/5/14 10:24:37 AM'640 |  |  |  |  |  |  |  |  |  |  |  | 3m 45s |  |  |  |  |  |  |  |  | L2 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/5/14 10:28:23 AM'471 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Report according to EN 50160 2011 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Timeframe:9/1/14 12:00 AM - 3/1/15 11:59 PM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 26 / |  |  | 31 |  |  |  |  |  |  |
|  |  |  | Starttime |  |  |  |  |  |  |  |  |  |  |  | Length |  |  |  |  |  |  |  |  | Input |  |  | Eventtype |  |  |  |  |  | Limit |  |  |  |  | Min |  |  |  |  |  | Avg |  | Max |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Endtime |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/16/14 3:15:47 PM'445 |  |  |  |  |  |  |  |  |  |  |  | 2m 12s |  |  |  |  |  |  |  |  | L2 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/16/14 3:18:00 PM'266 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/26/14 1:30:35 PM'365 |  |  |  |  |  |  |  |  |  |  |  | 29.303ms |  |  |  |  |  |  |  |  | L2 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/26/14 1:30:35 PM'395 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/26/14 1:30:36 PM'034 |  |  |  |  |  |  |  |  |  |  |  | 89.955ms |  |  |  |  |  |  |  |  | L2 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/26/14 1:30:36 PM'124 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/26/14 1:30:36 PM'651 |  |  |  |  |  |  |  |  |  |  |  | 178.257ms |  |  |  |  |  |  |  |  | L2 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/26/14 1:30:36 PM'829 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/26/14 1:30:37 PM'221 |  |  |  |  |  |  |  |  |  |  |  | 44m 37s |  |  |  |  |  |  |  |  | L2 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 5.95 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/26/14 2:15:14 PM'348 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/27/14 12:14:02 PM'278 |  |  |  |  |  |  |  |  |  |  |  | 49.752ms |  |  |  |  |  |  |  |  | L2 |  |  | Voltage outage |  |  |  |  |  | 10.30 |  |  |  |  | 0.00 |  |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/27/14 12:14:02 PM'328 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Report according to EN 50160 2011 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Timeframe:9/1/14 12:00 AM - 3/1/15 11:59 PM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 27 / |  |  | 31 |  |  |  |  |  |  |
|  |  | Overvoltage |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | 258 Events have been found. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | Residual voltage u % |  |  |  |  |  |  | Duration t ms |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 10 - 500ms |  |  |  |  |  |  | > 500ms |  |  |  | > 5s - 60s |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | > 110 - < 120 |  |  |  |  |  |  | 0 |  |  |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | 120 - % |  |  |  |  |  |  | 0 |  |  |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 258 out of ranges! |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 100 deepest events |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Starttime |  |  |  |  |  |  |  |  |  |  |  | Length |  |  |  |  |  |  |  |  | Input |  |  | Eventtype |  |  |  |  |  | Limit |  |  |  |  | Min |  |  |  |  |  | Avg |  | Max |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Endtime |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:15:10 AM'700 |  |  |  |  |  |  |  |  |  |  |  | 1.283s |  |  |  |  |  |  |  |  | L1 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 253.07 |  |  |  |  |  | 19337.74 |  | 21682.11 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:15:11 AM'983 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/3/14 3:22:54 PM'087 |  |  |  |  |  |  |  |  |  |  |  | 7m 59s |  |  |  |  |  |  |  |  | L3 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 253.07 |  |  |  |  |  | 12161.49 |  | 12334.55 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/3/14 3:30:53 PM'887 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/18/14 12:35:59 PM'762 |  |  |  |  |  |  |  |  |  |  |  | 411.616ms |  |  |  |  |  |  |  |  | L3 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 253.07 |  |  |  |  |  | 330.35 |  | 363.87 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/18/14 12:36:00 PM'174 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/26/14 6:37:27 PM'997 |  |  |  |  |  |  |  |  |  |  |  | 398.816ms |  |  |  |  |  |  |  |  | L1 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 253.14 |  |  |  |  |  | 330.94 |  | 362.80 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/26/14 6:37:28 PM'396 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/3/14 2:51:08 PM'177 |  |  |  |  |  |  |  |  |  |  |  | 329.401ms |  |  |  |  |  |  |  |  | L1 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 253.14 |  |  |  |  |  | 407.21 |  | 474.99 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/3/14 2:51:08 PM'506 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:02:39 AM'334 |  |  |  |  |  |  |  |  |  |  |  | 219.800ms |  |  |  |  |  |  |  |  | L3 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 253.21 |  |  |  |  |  | 271.47 |  | 284.39 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:02:39 AM'554 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:15:12 AM'024 |  |  |  |  |  |  |  |  |  |  |  | 499.349ms |  |  |  |  |  |  |  |  | L3 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 253.21 |  |  |  |  |  | 487.38 |  | 591.81 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:15:12 AM'523 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/29/14 9:55:47 AM'586 |  |  |  |  |  |  |  |  |  |  |  | 335.612ms |  |  |  |  |  |  |  |  | L2 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 253.28 |  |  |  |  |  | 302.52 |  | 328.63 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/29/14 9:55:47 AM'922 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/5/14 10:24:36 AM'716 |  |  |  |  |  |  |  |  |  |  |  | 159.056ms |  |  |  |  |  |  |  |  | L1 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 253.35 |  |  |  |  |  | 258.87 |  | 262.26 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/5/14 10:24:36 AM'876 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/3/14 12:39:31 PM'469 |  |  |  |  |  |  |  |  |  |  |  | 200.500ms |  |  |  |  |  |  |  |  | L1 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 253.35 |  |  |  |  |  | 263.68 |  | 270.17 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/3/14 12:39:31 PM'669 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/25/14 12:35:07 AM'086 |  |  |  |  |  |  |  |  |  |  |  | 30.001ms |  |  |  |  |  |  |  |  | L3 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 253.35 |  |  |  |  |  | 1024.93 |  | 1246.86 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/25/14 12:35:07 AM'116 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/27/14 12:14:02 PM'523 |  |  |  |  |  |  |  |  |  |  |  | 238.309ms |  |  |  |  |  |  |  |  | L1 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 253.42 |  |  |  |  |  | 270.56 |  | 281.58 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/27/14 12:14:02 PM'762 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:04:39 AM'205 |  |  |  |  |  |  |  |  |  |  |  | 194.700ms |  |  |  |  |  |  |  |  | L1 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 253.42 |  |  |  |  |  | 264.75 |  | 270.82 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:04:39 AM'400 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:40:52 AM'916 |  |  |  |  |  |  |  |  |  |  |  | 1.197s |  |  |  |  |  |  |  |  | L1 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 253.49 |  |  |  |  |  | 19852.81 |  | 20863.89 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:40:54 AM'113 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/3/14 12:39:31 PM'472 |  |  |  |  |  |  |  |  |  |  |  | 180.451ms |  |  |  |  |  |  |  |  | L2 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 253.49 |  |  |  |  |  | 259.14 |  | 262.53 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/3/14 12:39:31 PM'653 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/3/14 3:31:59 PM'206 |  |  |  |  |  |  |  |  |  |  |  | 3m 22s |  |  |  |  |  |  |  |  | L3 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 253.49 |  |  |  |  |  | 11999.04 |  | 12272.31 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/3/14 3:35:22 PM'083 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/27/14 12:14:02 PM'480 |  |  |  |  |  |  |  |  |  |  |  | 278.060ms |  |  |  |  |  |  |  |  | L3 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 253.56 |  |  |  |  |  | 278.80 |  | 294.65 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/27/14 12:14:02 PM'758 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:15:12 AM'054 |  |  |  |  |  |  |  |  |  |  |  | 468.748ms |  |  |  |  |  |  |  |  | L2 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 253.63 |  |  |  |  |  | 462.85 |  | 555.98 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:15:12 AM'523 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:11:01 AM'859 |  |  |  |  |  |  |  |  |  |  |  | 534.903ms |  |  |  |  |  |  |  |  | L2 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 253.70 |  |  |  |  |  | 451.21 |  | 548.20 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:11:02 AM'394 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/26/14 7:54:49 PM'283 |  |  |  |  |  |  |  |  |  |  |  | 8d 14h |  |  |  |  |  |  |  |  | L3 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 253.84 |  |  |  |  |  | 12177.55 |  | 23986.02 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/5/14 10:24:36 AM'366 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/5/14 10:24:36 AM'703 |  |  |  |  |  |  |  |  |  |  |  | 139.056ms |  |  |  |  |  |  |  |  | L3 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 253.84 |  |  |  |  |  | 257.57 |  | 259.28 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/5/14 10:24:36 AM'842 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/3/14 12:39:31 PM'455 |  |  |  |  |  |  |  |  |  |  |  | 190.350ms |  |  |  |  |  |  |  |  | L3 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 253.84 |  |  |  |  |  | 264.08 |  | 270.62 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/3/14 12:39:31 PM'646 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/3/14 2:51:08 PM'799 |  |  |  |  |  |  |  |  |  |  |  | 80.351ms |  |  |  |  |  |  |  |  | L1 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 253.97 |  |  |  |  |  | 255.36 |  | 256.40 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/3/14 2:51:08 PM'879 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:11:01 AM'869 |  |  |  |  |  |  |  |  |  |  |  | 524.750ms |  |  |  |  |  |  |  |  | L1 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 253.97 |  |  |  |  |  | 443.82 |  | 537.15 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:11:02 AM'394 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Report according to EN 50160 2011 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Timeframe:9/1/14 12:00 AM - 3/1/15 11:59 PM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 28 / |  |  | 31 |  |  |  |  |  |  |
|  |  |  | Starttime |  |  |  |  |  |  |  |  |  |  |  | Length |  |  |  |  |  |  |  |  | Input |  |  | Eventtype |  |  |  |  |  | Limit |  |  |  |  | Min |  |  |  |  |  | Avg |  | Max |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Endtime |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:15:12 AM'775 |  |  |  |  |  |  |  |  |  |  |  | 344.449ms |  |  |  |  |  |  |  |  | L1 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 253.97 |  |  |  |  |  | 311.51 |  | 341.04 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:15:13 AM'120 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/3/14 3:22:54 PM'093 |  |  |  |  |  |  |  |  |  |  |  | 7m 59s |  |  |  |  |  |  |  |  | L2 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 254.04 |  |  |  |  |  | 12114.01 |  | 12291.93 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/3/14 3:30:53 PM'874 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/26/14 7:54:49 PM'284 |  |  |  |  |  |  |  |  |  |  |  | 8d 14h |  |  |  |  |  |  |  |  | L2 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 254.18 |  |  |  |  |  | 12131.52 |  | 24898.43 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/5/14 10:24:36 AM'363 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/3/14 3:22:54 PM'090 |  |  |  |  |  |  |  |  |  |  |  | 7m 58s |  |  |  |  |  |  |  |  | L1 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 254.32 |  |  |  |  |  | 12101.96 |  | 12272.42 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/3/14 3:30:52 PM'890 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/27/14 12:14:02 PM'497 |  |  |  |  |  |  |  |  |  |  |  | 277.961ms |  |  |  |  |  |  |  |  | L2 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 254.32 |  |  |  |  |  | 282.52 |  | 300.53 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/27/14 12:14:02 PM'775 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/2/14 11:08:36 AM'907 |  |  |  |  |  |  |  |  |  |  |  | 361.414ms |  |  |  |  |  |  |  |  | L2 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 254.32 |  |  |  |  |  | 328.31 |  | 360.11 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/2/14 11:08:37 AM'268 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/3/14 2:51:08 PM'755 |  |  |  |  |  |  |  |  |  |  |  | 130.551ms |  |  |  |  |  |  |  |  | L3 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 254.32 |  |  |  |  |  | 261.32 |  | 265.55 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/3/14 2:51:08 PM'886 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/3/14 3:31:59 PM'212 |  |  |  |  |  |  |  |  |  |  |  | 3m 22s |  |  |  |  |  |  |  |  | L1 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 254.46 |  |  |  |  |  | 12058.05 |  | 12345.13 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/3/14 3:35:22 PM'187 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/3/14 3:31:59 PM'277 |  |  |  |  |  |  |  |  |  |  |  | 3m 22s |  |  |  |  |  |  |  |  | L2 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 254.46 |  |  |  |  |  | 12003.57 |  | 12271.18 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/3/14 3:35:21 PM'952 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/3/14 2:51:08 PM'174 |  |  |  |  |  |  |  |  |  |  |  | 319.450ms |  |  |  |  |  |  |  |  | L3 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 254.67 |  |  |  |  |  | 409.29 |  | 475.48 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/3/14 2:51:08 PM'493 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/29/14 9:56:42 AM'475 |  |  |  |  |  |  |  |  |  |  |  | 3d 4h |  |  |  |  |  |  |  |  | L1 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 254.81 |  |  |  |  |  | 12187.15 |  | 22987.90 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/1/14 2:09:48 PM'317 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/3/14 12:27:12 PM'419 |  |  |  |  |  |  |  |  |  |  |  | 31.352ms |  |  |  |  |  |  |  |  | L3 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 254.81 |  |  |  |  |  | 335.66 |  | 384.20 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/3/14 12:27:12 PM'450 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:03:10 AM'181 |  |  |  |  |  |  |  |  |  |  |  | 372.500ms |  |  |  |  |  |  |  |  | L3 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 254.81 |  |  |  |  |  | 322.88 |  | 355.31 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:03:10 AM'554 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:04:39 AM'185 |  |  |  |  |  |  |  |  |  |  |  | 184.349ms |  |  |  |  |  |  |  |  | L3 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 254.81 |  |  |  |  |  | 263.74 |  | 268.72 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:04:39 AM'370 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/3/14 2:51:08 PM'782 |  |  |  |  |  |  |  |  |  |  |  | 100.450ms |  |  |  |  |  |  |  |  | L2 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 254.88 |  |  |  |  |  | 257.64 |  | 259.62 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/3/14 2:51:08 PM'883 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:15:12 AM'755 |  |  |  |  |  |  |  |  |  |  |  | 364.702ms |  |  |  |  |  |  |  |  | L2 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 254.95 |  |  |  |  |  | 317.24 |  | 351.36 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:15:13 AM'120 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:02:39 AM'321 |  |  |  |  |  |  |  |  |  |  |  | 289.750ms |  |  |  |  |  |  |  |  | L2 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 255.09 |  |  |  |  |  | 285.75 |  | 302.87 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:02:39 AM'610 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:04:39 AM'183 |  |  |  |  |  |  |  |  |  |  |  | 215.100ms |  |  |  |  |  |  |  |  | L2 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 255.09 |  |  |  |  |  | 268.26 |  | 275.48 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:04:39 AM'398 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:02:38 AM'517 |  |  |  |  |  |  |  |  |  |  |  | 498.250ms |  |  |  |  |  |  |  |  | L3 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 255.09 |  |  |  |  |  | 452.73 |  | 535.60 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:02:39 AM'015 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:11:02 AM'678 |  |  |  |  |  |  |  |  |  |  |  | 303.900ms |  |  |  |  |  |  |  |  | L1 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 255.16 |  |  |  |  |  | 293.08 |  | 314.61 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:11:02 AM'982 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/1/14 2:09:48 PM'524 |  |  |  |  |  |  |  |  |  |  |  | 365.815ms |  |  |  |  |  |  |  |  | L2 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 255.29 |  |  |  |  |  | 329.55 |  | 361.09 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/1/14 2:09:48 PM'890 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:11:02 AM'638 |  |  |  |  |  |  |  |  |  |  |  | 344.400ms |  |  |  |  |  |  |  |  | L3 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 255.36 |  |  |  |  |  | 301.35 |  | 325.61 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:11:02 AM'982 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:40:52 AM'916 |  |  |  |  |  |  |  |  |  |  |  | 1.197s |  |  |  |  |  |  |  |  | L2 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 255.57 |  |  |  |  |  | 967.85 |  | 2277.52 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:40:54 AM'113 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:20:15 AM'421 |  |  |  |  |  |  |  |  |  |  |  | 1.888s |  |  |  |  |  |  |  |  | L3 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 255.64 |  |  |  |  |  | 16160.59 |  | 18848.34 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:20:17 AM'310 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/18/14 12:35:59 PM'808 |  |  |  |  |  |  |  |  |  |  |  | 348.163ms |  |  |  |  |  |  |  |  | L1 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 255.71 |  |  |  |  |  | 308.60 |  | 331.47 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/18/14 12:36:00 PM'156 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:20:17 AM'531 |  |  |  |  |  |  |  |  |  |  |  | 171.049ms |  |  |  |  |  |  |  |  | L3 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 255.71 |  |  |  |  |  | 425.14 |  | 506.66 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:20:17 AM'702 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/26/14 1:30:35 PM'519 |  |  |  |  |  |  |  |  |  |  |  | 354.014ms |  |  |  |  |  |  |  |  | L1 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 255.78 |  |  |  |  |  | 316.85 |  | 345.42 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/26/14 1:30:35 PM'873 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/2/14 11:08:36 AM'200 |  |  |  |  |  |  |  |  |  |  |  | 497.719ms |  |  |  |  |  |  |  |  | L1 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 255.99 |  |  |  |  |  | 515.96 |  | 614.13 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/2/14 11:08:36 AM'698 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:15:12 AM'034 |  |  |  |  |  |  |  |  |  |  |  | 489.199ms |  |  |  |  |  |  |  |  | L1 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 255.99 |  |  |  |  |  | 464.45 |  | 561.33 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:15:12 AM'523 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/3/14 12:27:13 PM'156 |  |  |  |  |  |  |  |  |  |  |  | 383.315ms |  |  |  |  |  |  |  |  | L1 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 256.05 |  |  |  |  |  | 329.49 |  | 362.90 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/3/14 12:27:13 PM'539 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:11:02 AM'678 |  |  |  |  |  |  |  |  |  |  |  | 293.799ms |  |  |  |  |  |  |  |  | L2 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 256.05 |  |  |  |  |  | 289.32 |  | 308.66 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:11:02 AM'972 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/1/14 2:09:48 PM'497 |  |  |  |  |  |  |  |  |  |  |  | 386.165ms |  |  |  |  |  |  |  |  | L3 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 256.40 |  |  |  |  |  | 334.66 |  | 369.42 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/1/14 2:09:48 PM'883 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/26/14 6:37:27 PM'974 |  |  |  |  |  |  |  |  |  |  |  | 399.115ms |  |  |  |  |  |  |  |  | L3 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 256.68 |  |  |  |  |  | 332.11 |  | 364.55 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/26/14 6:37:28 PM'373 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/5/14 10:24:36 AM'680 |  |  |  |  |  |  |  |  |  |  |  | 238.359ms |  |  |  |  |  |  |  |  | L2 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 256.74 |  |  |  |  |  | 273.42 |  | 281.01 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/5/14 10:24:36 AM'919 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:02:39 AM'317 |  |  |  |  |  |  |  |  |  |  |  | 309.749ms |  |  |  |  |  |  |  |  | L1 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 256.88 |  |  |  |  |  | 289.87 |  | 308.94 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:02:39 AM'627 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Report according to EN 50160 2011 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Timeframe:9/1/14 12:00 AM - 3/1/15 11:59 PM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 29 / |  |  | 31 |  |  |  |  |  |  |
|  |  |  | Starttime |  |  |  |  |  |  |  |  |  |  |  | Length |  |  |  |  |  |  |  |  | Input |  |  | Eventtype |  |  |  |  |  | Limit |  |  |  |  | Min |  |  |  |  |  | Avg |  | Max |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Endtime |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/25/14 12:35:04 AM'197 |  |  |  |  |  |  |  |  |  |  |  | 879.834ms |  |  |  |  |  |  |  |  | L3 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 256.88 |  |  |  |  |  | 866.10 |  | 1285.08 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/25/14 12:35:05 AM'077 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/25/14 12:35:07 AM'276 |  |  |  |  |  |  |  |  |  |  |  | 200.004ms |  |  |  |  |  |  |  |  | L3 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 256.88 |  |  |  |  |  | 708.28 |  | 1336.23 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/25/14 12:35:07 AM'476 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/2/14 11:08:36 AM'881 |  |  |  |  |  |  |  |  |  |  |  | 390.615ms |  |  |  |  |  |  |  |  | L3 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 256.88 |  |  |  |  |  | 335.77 |  | 370.08 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/2/14 11:08:37 AM'271 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/3/14 12:27:13 PM'121 |  |  |  |  |  |  |  |  |  |  |  | 414.530ms |  |  |  |  |  |  |  |  | L3 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 256.88 |  |  |  |  |  | 349.04 |  | 392.03 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/3/14 12:27:13 PM'535 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/29/14 9:55:47 AM'590 |  |  |  |  |  |  |  |  |  |  |  | 305.062ms |  |  |  |  |  |  |  |  | L3 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 256.95 |  |  |  |  |  | 295.61 |  | 318.58 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/29/14 9:55:47 AM'895 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/26/14 6:37:27 PM'981 |  |  |  |  |  |  |  |  |  |  |  | 409.016ms |  |  |  |  |  |  |  |  | L2 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 257.02 |  |  |  |  |  | 336.61 |  | 372.28 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/26/14 6:37:28 PM'390 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:04:38 AM'367 |  |  |  |  |  |  |  |  |  |  |  | 497.750ms |  |  |  |  |  |  |  |  | L2 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 257.02 |  |  |  |  |  | 446.20 |  | 532.79 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:04:38 AM'865 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/29/14 9:55:46 AM'929 |  |  |  |  |  |  |  |  |  |  |  | 409.166ms |  |  |  |  |  |  |  |  | L1 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 257.09 |  |  |  |  |  | 458.32 |  | 542.03 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/29/14 9:55:47 AM'339 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/3/14 2:51:08 PM'170 |  |  |  |  |  |  |  |  |  |  |  | 329.400ms |  |  |  |  |  |  |  |  | L2 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 257.23 |  |  |  |  |  | 405.64 |  | 474.99 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/3/14 2:51:08 PM'500 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:15:12 AM'765 |  |  |  |  |  |  |  |  |  |  |  | 314.051ms |  |  |  |  |  |  |  |  | L3 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 257.29 |  |  |  |  |  | 302.41 |  | 326.47 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:15:13 AM'079 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/29/14 9:55:47 AM'593 |  |  |  |  |  |  |  |  |  |  |  | 345.662ms |  |  |  |  |  |  |  |  | L1 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 257.50 |  |  |  |  |  | 306.93 |  | 332.64 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/29/14 9:55:47 AM'938 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:20:17 AM'531 |  |  |  |  |  |  |  |  |  |  |  | 161.000ms |  |  |  |  |  |  |  |  | L1 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 257.71 |  |  |  |  |  | 409.81 |  | 482.49 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:20:17 AM'692 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/3/14 12:27:13 PM'149 |  |  |  |  |  |  |  |  |  |  |  | 383.415ms |  |  |  |  |  |  |  |  | L2 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 257.77 |  |  |  |  |  | 336.08 |  | 373.08 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/3/14 12:27:13 PM'532 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/18/14 12:35:59 PM'048 |  |  |  |  |  |  |  |  |  |  |  | 498.320ms |  |  |  |  |  |  |  |  | L2 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 257.91 |  |  |  |  |  | 457.59 |  | 552.21 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/18/14 12:35:59 PM'546 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/26/14 1:30:35 PM'486 |  |  |  |  |  |  |  |  |  |  |  | 383.414ms |  |  |  |  |  |  |  |  | L3 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 257.98 |  |  |  |  |  | 336.03 |  | 370.42 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/26/14 1:30:35 PM'870 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:04:38 AM'349 |  |  |  |  |  |  |  |  |  |  |  | 507.901ms |  |  |  |  |  |  |  |  | L3 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 258.46 |  |  |  |  |  | 459.52 |  | 547.87 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:04:38 AM'857 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/2/14 11:08:36 AM'913 |  |  |  |  |  |  |  |  |  |  |  | 371.014ms |  |  |  |  |  |  |  |  | L1 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 258.60 |  |  |  |  |  | 328.20 |  | 358.73 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/2/14 11:08:37 AM'284 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/25/14 12:35:07 AM'216 |  |  |  |  |  |  |  |  |  |  |  | 50.003ms |  |  |  |  |  |  |  |  | L3 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 258.87 |  |  |  |  |  | 802.43 |  | 1183.43 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/25/14 12:35:07 AM'266 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 3:01:42 AM'175 |  |  |  |  |  |  |  |  |  |  |  | 19.999ms |  |  |  |  |  |  |  |  | L2 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 259.35 |  |  |  |  |  | 296.44 |  | 329.39 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 3:01:42 AM'195 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/16/14 3:18:00 PM'267 |  |  |  |  |  |  |  |  |  |  |  | 8d 9h |  |  |  |  |  |  |  |  | L3 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 259.62 |  |  |  |  |  | 12093.12 |  | 21505.55 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/25/14 12:35:02 AM'657 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:03:08 AM'625 |  |  |  |  |  |  |  |  |  |  |  | 1.346s |  |  |  |  |  |  |  |  | L3 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 259.69 |  |  |  |  |  | 16275.52 |  | 19802.84 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:03:09 AM'971 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:02:38 AM'534 |  |  |  |  |  |  |  |  |  |  |  | 478.250ms |  |  |  |  |  |  |  |  | L2 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 259.96 |  |  |  |  |  | 430.02 |  | 509.10 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:02:39 AM'012 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/26/14 1:30:34 PM'820 |  |  |  |  |  |  |  |  |  |  |  | 467.518ms |  |  |  |  |  |  |  |  | L2 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 260.16 |  |  |  |  |  | 505.54 |  | 598.35 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/26/14 1:30:35 PM'287 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/11/14 9:44:08 AM'047 |  |  |  |  |  |  |  |  |  |  |  | 29.701ms |  |  |  |  |  |  |  |  | L2 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 260.37 |  |  |  |  |  | 459.59 |  | 562.55 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/11/14 9:44:08 AM'077 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/25/14 12:35:09 AM'116 |  |  |  |  |  |  |  |  |  |  |  | 249.961ms |  |  |  |  |  |  |  |  | L3 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 260.50 |  |  |  |  |  | 475.03 |  | 776.79 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/25/14 12:35:09 AM'366 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/1/14 2:09:48 PM'541 |  |  |  |  |  |  |  |  |  |  |  | 345.363ms |  |  |  |  |  |  |  |  | L1 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 260.71 |  |  |  |  |  | 319.19 |  | 345.27 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/1/14 2:09:48 PM'886 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/18/14 12:35:59 PM'791 |  |  |  |  |  |  |  |  |  |  |  | 379.814ms |  |  |  |  |  |  |  |  | L2 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 260.84 |  |  |  |  |  | 322.99 |  | 350.91 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/18/14 12:36:00 PM'170 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/26/14 9:32:27 AM'943 |  |  |  |  |  |  |  |  |  |  |  | 411.616ms |  |  |  |  |  |  |  |  | L1 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 261.05 |  |  |  |  |  | 400.60 |  | 472.61 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/26/14 9:32:28 AM'355 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:03:10 AM'216 |  |  |  |  |  |  |  |  |  |  |  | 352.649ms |  |  |  |  |  |  |  |  | L1 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 261.18 |  |  |  |  |  | 314.33 |  | 342.90 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:03:10 AM'569 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/3/14 12:39:30 PM'656 |  |  |  |  |  |  |  |  |  |  |  | 468.201ms |  |  |  |  |  |  |  |  | L2 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 261.25 |  |  |  |  |  | 449.05 |  | 527.82 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/3/14 12:39:31 PM'125 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/3/14 12:27:12 PM'436 |  |  |  |  |  |  |  |  |  |  |  | 31.351ms |  |  |  |  |  |  |  |  | L2 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 261.66 |  |  |  |  |  | 403.63 |  | 462.35 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/3/14 12:27:12 PM'468 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 7:20:01 AM'107 |  |  |  |  |  |  |  |  |  |  |  | 42d 7h |  |  |  |  |  |  |  |  | L3 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 261.66 |  |  |  |  |  | 12172.86 |  | 19415.38 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 3/14/15 2:33:43 PM'094 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:03:10 AM'181 |  |  |  |  |  |  |  |  |  |  |  | 412.701ms |  |  |  |  |  |  |  |  | L2 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 261.99 |  |  |  |  |  | 337.29 |  | 375.82 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 1:03:10 AM'594 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/18/14 12:35:59 PM'052 |  |  |  |  |  |  |  |  |  |  |  | 477.068ms |  |  |  |  |  |  |  |  | L3 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 262.13 |  |  |  |  |  | 459.36 |  | 545.54 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 9/18/14 12:35:59 PM'529 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/3/14 8:38:23 AM'479 |  |  |  |  |  |  |  |  |  |  |  | 418.275ms |  |  |  |  |  |  |  |  | L1 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 262.73 |  |  |  |  |  | 436.51 |  | 540.63 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 12/3/14 8:38:23 AM'897 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Report according to EN 50160 2011 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Timeframe:9/1/14 12:00 AM - 3/1/15 11:59 PM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 30 / |  |  | 31 |  |  |  |  |  |  |
|  |  |  | Starttime |  |  |  |  |  |  |  |  |  |  |  | Length |  |  |  |  |  |  |  |  | Input |  |  | Eventtype |  |  |  |  |  | Limit |  |  |  |  | Min |  |  |  |  |  | Avg |  | Max |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Endtime |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/26/14 1:30:35 PM'503 |  |  |  |  |  |  |  |  |  |  |  | 383.416ms |  |  |  |  |  |  |  |  | L2 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 263.07 |  |  |  |  |  | 334.61 |  | 368.02 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/26/14 1:30:35 PM'886 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 3:52:51 AM'323 |  |  |  |  |  |  |  |  |  |  |  | 20.400ms |  |  |  |  |  |  |  |  | L3 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 263.27 |  |  |  |  |  | 267.34 |  | 271.34 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/31/15 3:52:51 AM'343 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/10/15 12:57:07 PM'921 |  |  |  |  |  |  |  |  |  |  |  | 1m 33s |  |  |  |  |  |  |  |  | L2 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 263.41 |  |  |  |  |  | 12195.76 |  | 21124.72 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/10/15 12:58:41 PM'308 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/10/15 12:58:41 PM'305 |  |  |  |  |  |  |  |  |  |  |  | 20.101ms |  |  |  |  |  |  |  |  | L1 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 263.54 |  |  |  |  |  | 269.25 |  | 274.84 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1/10/15 12:58:41 PM'325 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/2/14 11:08:36 AM'223 |  |  |  |  |  |  |  |  |  |  |  | 467.867ms |  |  |  |  |  |  |  |  | L2 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 263.88 |  |  |  |  |  | 520.09 |  | 617.11 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 11/2/14 11:08:36 AM'691 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/27/14 12:14:01 PM'661 |  |  |  |  |  |  |  |  |  |  |  | 533.470ms |  |  |  |  |  |  |  |  | L1 |  |  | Over voltage |  |  |  |  |  | 253.00 |  |  |  |  | 264.01 |  |  |  |  |  | 438.93 |  | 512.80 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 10/27/14 12:14:02 PM'195 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Report according to EN 50160 2011 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Timeframe:9/1/14 12:00 AM - 3/1/15 11:59 PM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 31 / |  |  | 31 |  |  |  |  |  |  |
|  |  | Janitza-GridVis 4.0.2(2013-05-28_14-34-52) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |